## Slide 1: Modern Boiler Level Indication
“Real Time Density Corrected Level Measurement”

## Slide 2
Modern Boiler Level Indication
Different Types of High-Pressure Steam, Boiler Level Indicators ?
DP Transmitter
Multi-Point Probe Level Indicator
Guided Wave Radar
Sight Glass
- Widely recognized as superior
level technology
- Endless Recalibration
- Classic Reliable
- Must have per code
- Direct Reading
- Level Verification

## Slide 3
Modern Boiler Level Indication GWR v. DP
Guided Wave
Straight Forward: Reads Level by Evaluating Echo
Quest-Tec offers a simple means of virtual, real time Temperature Compensation
Simple Mechanical Installation: Drum Connections and Drain
Virtually maintenance free
Enhanced accuracy during fill and start-up.
Infers level via calculation of Pressure Differences
Temperature compensation is resolved via a complex algorithm based on assumptions of temperature drop.
Complex system of pressurized communication piping
Frequent maintenance of piping
Relies on pressure balancing of system which slows response
Differential Pressure

## Slide 4
What is a Guided Wave
Guided Wave Radar is a highly accurate means of determining Liquid Level
Microwave Burst Tracks a SS Rod
Using Time Domain Reflectometry (TDR), Return Echo is Evaluated
Guided Wave Radar – Steam Drums
Modern Boiler Level Indication

## Slide 5
Gas Phase Compensation vs. Density Correction
Modern Boiler Level Indication

## Slide 6
What is a Gas Phase Compensation?
Microwaves Travel Slower thru Steam
Higher Pressure, Slower Speed
Known Length Reference Point Reflector
Calculates a Dynamic Compensation
Guided Wave Radar – Steam Drums

## Slide 7
What is a Water Density Compensation?
The sub-cooled condensed steam in the bypass chamber is denser than the water in the drum
GWR is accurate, but will pass along an error of 5-18%, due cooler/denser water in the bypass chamber
Guided Wave Radar – Steam Drums
Density Error

## Slide 8
Water Density Math
Guided Wave Radar – Steam Drums
Density Error
Hs
Hd
HdDd = HgDg + HsDs
Hd =
Hg(Dg - Ds)
Dd - Ds
Hg
Density = Ds
Dd

## Slide 9
Water Density
Guided Wave Radar technology with Density Error Correction
DENSITY ERROR
- Real time temperature reading sent to control unit
- Density error is calculated
- Level signal is corrected
- Accuracy is improved

## Slide 10
What Challenges Exist In High Pressure Steam Service, When Measuring Water Level?
Condensate Flow
What is the Error Potential?
Modern Boiler Level Indication
Pressure | Temperature | Column Range | *Density Error % | *Density Error “inches” of H2O
2000 psi | 636 F | 60” | 8% | 4”
2500 psi | 669 F | 60” | 12% | 7”
3000 psi | 696 F | 60” | 27% | 18”
*Numbers are rounded up.
1
2
3
4

## Slide 11
Field Installation
Field Proven Approach
Duke Buck Steam Station
Duke Dan River
Sugar Creek Generating Station
Duke - Asheville
Alliant Riverside
NAES Newark Energy Center
Alliant Marshalltown
Duke – Tiger Bay
Duke Hines Energy Complex
Covert Generating Station
BP Whiting Clean Energy

## Slide 12
Always Use Coaxial Probe
Guided Wave Radar – Steam Drums
Presentation By: Questtec Solutions, Houston Texas
Bare Probe
Coax Probe
Wave will ignore irregularities on the column wall.
Cost is nominal for the benefit.
XXX

## Slide 13
The Quest-Tec Advantage
Why Quest-Tec
Quest-Tec Specializes in the Stem Drum Level Indication – Over 10 years Experience with successful HP Steam Drum Applications
Quest-Tec fully understands and compensates for Water Density Error
Quest-Tec products are designed for ease of installation/integration
Quest-Tec is dedicated the high level of personal service your operation requires
Quest-Tec stocks all long lead time items (including complete HP Guided Wave probes and electronics) and will keep your plant running
Quest-Tec is THE quality supplier of Steam Drum Water Level Indication equipment
  Direct Reading Sight Glasses
  Conductivity/Resistivity Remote Level Indicators
  Fully integrated Guided Wave Radar systems.
QUEST-TEC SOLUTIONS IS AN ASME CODE STAMP HOLDER, S, R, U
S Stamp. The ASME stamp allows manufacturers to fabricate ASME-compliant pressure retaining parts, power boilers, and power piping. Like the U and U2 stamps, it requires a quality assurance program that meets the standards outlined in the ASME Boiler and Pressure Vessel Code.